## Register Description V1.0
Mobile 1 Channel Telemetry Modbus register description for Software version 1.2
					Integer value limitations
Input Registers					- Measurement index is running number of measurement (from the power up)
Input Registers (16-bit integer)				Input Registers (32-bit integer)				Input Registers single presicion floating point					- 16-bit integer register overflows at 32678 and next value is 0. 32678 is the maximum value of 16-bit signed integer
RF Device independent Measurement values				RF Device independent Measurement values				RF Device independent Measurement values					- 32-bit register overflows at 2147483648 and next value is 0. 2147483648 is the maximum value of 32-bit signed integer
Register	Type	Description		Register	Type	Description		Register	Type	Description					- 32-bit single precision floating point dynamic range for full precision integer value is -16777216 .. 16777216
30001	unsigned singed 16-bit	Battery Voltage [0.01V]		31001	unsigned singed 32-bit	Battery Voltage [0.01V]		32001	Single Precision Floating Point	Battery Voltage [V]
30002	unsigned singed 16-bit	Battery Capacity [0.01%]		31003	unsigned singed 32-bit	Battery Capacity [0.01%]		32003	Single Precision Floating Point	Battery Capacity [%]					Modbus register byte / bit order. Modbus Word size is 16bits
30003	unsigned singed 16-bit	Battery Charger State		31005	unsigned singed 32-bit	Battery Charger State		32005	Single Precision Floating Point	Battery Charger State					Byte (8-bit) bit order is lsb
30004	unsigned singed 16-bit	CPU Temperature [0.1°C]		31007	unsigned singed 32-bit	CPU Temperature [0.1°C]		32007	Single Precision Floating Point	CPU Temperature [°C]					bit 0	bit 1	bit 2	bit 3	bit 4	bit 5	bit 6	bit 7
30005	unsigned singed 16-bit	Buttons State		31009	unsigned singed 32-bit	Buttons State		32009	Single Precision Floating Point	Buttons State
30006	unsigned singed 16-bit	PWM Clock [10kHz]		31011	unsigned singed 32-bit	PWM Clock [Hz]		32011	Single Precision Floating Point	PWM Clock [Hz]	<-	Source Clock for PWM Module			16-bit Integer (Big Endian)			32-bit Integer / 32-bit Floating point
30007	unsigned singed 16-bit	PWM Frequency [Hz]		31013	unsigned singed 32-bit	PWM Frequency [Hz]		32013	Single Precision Floating Point	PWM Frequency [Hz]					MSB	LSB		Register N		Register N+1
30008	unsigned singed 16-bit	PWM Channel 1 Duty Cycle [0.01%]		31015	unsigned singed 32-bit	PWM Channel 1 Duty Cycle [0.01%]		32015	Single Precision Floating Point	PWM Channel 1 Duty Cycle [%]					Byte1	Byte0 (LSB)	Byte3 (MSB)	Byte2
30009	unsigned singed 16-bit	PWM Channel 2 Duty Cycle [0.01%]		31017	unsigned singed 32-bit	PWM Channel 2 Duty Cycle [0.01%]		32017	Single Precision Floating Point	PWM Channel 2 Duty Cycle [%]
30010	unsigned singed 16-bit	PWM Channel 3 Duty Cycle [0.01%]		31019	unsigned singed 32-bit	PWM Channel 3 Duty Cycle [0.01%]		32019	Single Precision Floating Point	PWM Channel 3 Duty Cycle [%]
30011	unsigned singed 16-bit	PWM Channel 4 Duty Cycle [0.01%]		31021	unsigned singed 32-bit	PWM Channel 4 Duty Cycle [0.01%]		32021	Single Precision Floating Point	PWM Channel 4 Duty Cycle [%]
30012	unsigned singed 16-bit	Reserved(/Debug Information)		31023	unsigned singed 32-bit	Reserved(/Debug Information)		32023	Single Precision Floating Point	Reserved(/Debug Information)
30013	unsigned singed 16-bit	Reserved(/Debug Information)		31025	unsigned singed 32-bit	Reserved(/Debug Information)		32025	Single Precision Floating Point	Reserved(/Debug Information)
30014	unsigned singed 16-bit	Reserved(/Debug Information)		31027	unsigned singed 32-bit	Reserved(/Debug Information)		32027	Single Precision Floating Point	Reserved(/Debug Information)
30015	unsigned singed 16-bit	Reserved		31029	unsigned singed 32-bit	Reserved		32029	Single Precision Floating Point	Reserved
30016	unsigned singed 16-bit	Reserved		31031	unsigned singed 32-bit	Reserved		32031	Single Precision Floating Point	Reserved
30017	unsigned singed 16-bit	Reserved		31033	unsigned singed 32-bit	Reserved		32033	Single Precision Floating Point	Reserved
30018	unsigned singed 16-bit	Reserved		31035	unsigned singed 32-bit	Reserved		32035	Single Precision Floating Point	Reserved
30019	unsigned singed 16-bit	Reserved		31037	unsigned singed 32-bit	Reserved		32037	Single Precision Floating Point	Reserved
30020	unsigned singed 16-bit	Reserved		31039	unsigned singed 32-bit	Reserved		32039	Single Precision Floating Point	Reserved
30021	unsigned singed 16-bit	Reserved		31041	unsigned singed 32-bit	Reserved		32041	Single Precision Floating Point	Reserved
30022	unsigned singed 16-bit	Reserved		31043	unsigned singed 32-bit	Reserved		32043	Single Precision Floating Point	Reserved
30023	unsigned singed 16-bit	Reserved		31045	unsigned singed 32-bit	Reserved		32045	Single Precision Floating Point	Reserved
30024	unsigned singed 16-bit	Reserved		31047	unsigned singed 32-bit	Reserved		32047	Single Precision Floating Point	Reserved
30025	unsigned singed 16-bit	Reserved		31049	unsigned singed 32-bit	Reserved		32049	Single Precision Floating Point	Reserved

Input Registers (16-bit integer)				Input Registers (32-bit integer)				Input Registers single presicion floating point
Thermo Couple 8 and 16 Channel Measurement values				Thermo Couple 8 and 16 Channel Measurement values				Thermo Couple 8 and 16 Channel Measurement values
Register	Type	Description		Register	Type	Description		Register	Type	Description
30026	unsinged 16-bit	Packet Index (16-bit value)		31051	unsinged 32-bit	Packet Index (16-bit value)		32051	Single Precision Floating Point	Packet Index (16-bit value)	<-	Radio incoming Packet Index, or actually running index of the expected incoming packet
30027	unsinged 16-bit	Radio Rx Status		31053	unsinged 32-bit	Radio Rx Status		32053	Single Precision Floating Point	Radio Rx Status	<-	Radio Rx Status: Binary coded Receive Status: Radio 1 has received packet bit 0 = 1 otherwise 0, Radio 2 has received packet bit 1 = 1 otherwise 0
30028	unsinged 16-bit	Receive Success [%]		31055	unsinged 32-bit	Receive Success [%]		32055	Single Precision Floating Point	Receive Success [%]
30029	unsinged 16-bit	Data Valid [0 -> Valid, !0 -> Valid]		31057	unsinged 32-bit	Data Valid [0 -> Valid, !0 -> Valid]		32057	Single Precision Floating Point	Data Valid [0 -> Valid, !0 -> Valid]	<-	Boolean value: False = 0, True = not 0
30030	unsinged 16-bit	Data Validation Counter		31059	unsinged 32-bit	Data Validation Counter		32059	Single Precision Floating Point	Data Validation Counter
30031	unsinged 16-bit	Reserved		31061	unsinged 32-bit	Reserved		32061	Single Precision Floating Point	Reserved
30032	unsinged 16-bit	Reserved		31063	unsinged 32-bit	Reserved		32063	Single Precision Floating Point	Reserved
30033	unsinged 16-bit	Reserved		31065	unsinged 32-bit	Reserved		32065	Single Precision Floating Point	Reserved
30034	unsinged 16-bit	Reserved		31067	unsinged 32-bit	Reserved		32067	Single Precision Floating Point	Reserved
30035	unsinged 16-bit	Reserved		31069	unsinged 32-bit	Reserved		32069	Single Precision Floating Point	Reserved
30036	singed 16-bit	Channel 1 [1/16°C]		31071	singed 32-bit	Channel 1 [1/16°C]		32071	Single Precision Floating Point	Channel 1 [°C]
30037	singed 16-bit	Channel 2 [1/16°C]		31073	singed 32-bit	Channel 2 [1/16°C]		32073	Single Precision Floating Point	Channel 2 [°C]
30038	singed 16-bit	Channel 3 [1/16°C]		31075	singed 32-bit	Channel 3 [1/16°C]		32075	Single Precision Floating Point	Channel 3 [°C]
30039	singed 16-bit	Channel 4 [1/16°C]		31077	singed 32-bit	Channel 4 [1/16°C]		32077	Single Precision Floating Point	Channel 4 [°C]
30040	singed 16-bit	Channel 5 [1/16°C]		31079	singed 32-bit	Channel 5 [1/16°C]		32079	Single Precision Floating Point	Channel 5 [°C]
30041	singed 16-bit	Channel 6 [1/16°C]		31081	singed 32-bit	Channel 6 [1/16°C]		32081	Single Precision Floating Point	Channel 6 [°C]
30042	singed 16-bit	Channel 7 [1/16°C]		31083	singed 32-bit	Channel 7 [1/16°C]		32083	Single Precision Floating Point	Channel 7 [°C]
30043	singed 16-bit	Channel 8 [1/16°C]		31085	singed 32-bit	Channel 8 [1/16°C]		32085	Single Precision Floating Point	Channel 8 [°C]
30044	singed 16-bit	Channel 9 / Reference 1 [1/16°C]		31087	singed 32-bit	Channel 9 / Reference 1 [1/16°C]		32087	Single Precision Floating Point	Channel 9 / Reference 1 [°C]
30045	singed 16-bit	Channel 10 / Reference 2 [1/16°C]		31089	singed 32-bit	Channel 10 / Reference 2 [1/16°C]		32089	Single Precision Floating Point	Channel 10 / Reference 2 [°C]
30046	singed 16-bit	Channel 11 / Reference 3 [1/16°C]		31091	singed 32-bit	Channel 11 / Reference 3 [1/16°C]		32091	Single Precision Floating Point	Channel 11 / Reference 3 [°C]
30047	singed 16-bit	Channel 12 / Reference 4 [1/16°C]		31093	singed 32-bit	Channel 12 / Reference 4 [1/16°C]		32093	Single Precision Floating Point	Channel 12 / Reference 4 [°C]
30048	singed 16-bit	Channel 13 / Reference 5 [1/16°C]		31095	singed 32-bit	Channel 13 / Reference 5 [1/16°C]		32095	Single Precision Floating Point	Channel 13 / Reference 5 [°C]
30049	singed 16-bit	Channel 14 / Reference 6 [1/16°C]		31097	singed 32-bit	Channel 14 / Reference 6 [1/16°C]		32097	Single Precision Floating Point	Channel 14 / Reference 6 [°C]
30050	singed 16-bit	Channel 15 / Reference 7 [1/16°C]		31099	singed 32-bit	Channel 15 / Reference 7 [1/16°C]		32099	Single Precision Floating Point	Channel 15 / Reference 7 [°C]
30051	singed 16-bit	Channel 16 / Reference 8 [1/16°C]		31101	singed 32-bit	Channel 16 / Reference 8 [1/16°C]		32101	Single Precision Floating Point	Channel 16 / Reference 8 [°C]

Input Registers (16-bit integer)				Input Registers (32-bit integer)				Input Registers single presicion floating point
Thermo Couple 4 Channel Measurement values				Thermo Couple 4 Channel Measurement values				Thermo Couple 4 Channel Measurement values
Register	Type	Description		Register	Type	Description		Register	Type	Description
30026	unsinged 16-bit	Packet Index (16-bit value)		31051	unsinged 32-bit	Packet Index (16-bit value)		32051	Single Precision Floating Point	Packet Index (16-bit value)	<-	Radio incoming Packet Index, or actually running index of the expected incoming packet
30027	unsinged 16-bit	Radio Rx Status		31053	unsinged 32-bit	Radio Rx Status		32053	Single Precision Floating Point	Radio Rx Status	<-	Radio Rx Status: Binary coded Receive Status: Radio 1 has received packet bit 0 = 1 otherwise 0, Radio 2 has received packet bit 1 = 1 otherwise 0
30028	unsinged 16-bit	Receive Success [%]		31055	unsinged 32-bit	Receive Success [%]		32055	Single Precision Floating Point	Receive Success [%]
30029	unsinged 16-bit	Data Valid [0 -> Valid, !0 -> Valid]		31057	unsinged 32-bit	Data Valid [0 -> Valid, !0 -> Valid]		32057	Single Precision Floating Point	Data Valid [0 -> Valid, !0 -> Valid]	<-	Boolean value: False = 0, True = not 0
30030	unsinged 16-bit	Data Validation Counter		31059	unsinged 32-bit	Data Validation Counter		32059	Single Precision Floating Point	Data Validation Counter
30031	unsinged 16-bit	Reserved		31061	unsinged 32-bit	Reserved		32061	Single Precision Floating Point	Reserved
30032	unsinged 16-bit	Reserved		31063	unsinged 32-bit	Reserved		32063	Single Precision Floating Point	Reserved
30033	unsinged 16-bit	Reserved		31065	unsinged 32-bit	Reserved		32065	Single Precision Floating Point	Reserved
30034	unsinged 16-bit	Reserved		31067	unsinged 32-bit	Reserved		32067	Single Precision Floating Point	Reserved
30035	unsinged 16-bit	Reserved		31069	unsinged 32-bit	Reserved		32069	Single Precision Floating Point	Reserved
30036	singed 16-bit	Channel 1 [1/16°C]		31071	singed 32-bit	Channel 1 [1/16°C]		32071	Single Precision Floating Point	Channel 1 [°C]
30037	singed 16-bit	Channel 2 [1/16°C]		31073	singed 32-bit	Channel 2 [1/16°C]		32073	Single Precision Floating Point	Channel 2 [°C]
30038	singed 16-bit	Channel 3 [1/16°C]		31075	singed 32-bit	Channel 3 [1/16°C]		32075	Single Precision Floating Point	Channel 3 [°C]
30039	singed 16-bit	Channel 4 [1/16°C]		31077	singed 32-bit	Channel 4 [1/16°C]		32077	Single Precision Floating Point	Channel 4 [°C]
30040	singed 16-bit	Reference 1 and 2 [1/16°C]		31079	singed 32-bit	Reference 1 and 2 [1/16°C]		32079	Single Precision Floating Point	Reference 1 and 2 [°C]
30041	singed 16-bit	Reference 3 and 4 [1/16°C]		31081	singed 32-bit	Reference 3 and 4 [1/16°C]		32081	Single Precision Floating Point	Reference 3 and 4 [°C]

Input Registers (16-bit integer)				Input Registers (32-bit integer)				Input Registers single presicion floating point
Remote Mux/Switch				Remote Mux/Switch				Remote Mux/Switch
Register	Type	Description		Register	Type	Description		Register	Type	Description
30026	unsinged 16-bit	1st Device Type		31051	unsinged 32-bit	1st Device Type		32051	Single Precision Floating Point	1st Device Type	<-	Device type: 1 -> Switch, 2 -> Mux
30027	unsinged 16-bit	1st Device ID		31053	unsinged 32-bit	1st Device ID		32053	Single Precision Floating Point	1st Device ID
30028	unsinged 16-bit	Time since last Rx [s]		31055	unsinged 32-bit	Time since last Rx [s]		32055	Single Precision Floating Point	Time since last Rx [s]	<-	Time since last received packet. Device will be deleted if no packet received in 2 minutes
30029	unsinged 16-bit	Switch State		31057	unsinged 32-bit	Switch State		32057	Single Precision Floating Point	Switch State	<-	bits 0..6 indicate switch/mux states, bit 7 indicates transmit interval
30030	unsinged 16-bit	Temperature [1/128°C]		31059	unsinged 32-bit	Temperature [1/128°C]		32059	Single Precision Floating Point	Temperature [°C]		- For switches bit value 0 -> switch off, bit value 1 -> switch on.
30031	unsinged 16-bit	Input Voltage [0.01V]		31061	unsinged 32-bit	Input Voltage [0.01V]		32061	Single Precision Floating Point	Input Voltage [V]		- For muxes bit value 0 -> CH1 selected , bit value 1 -> CH2 selected
30032	unsinged 16-bit	Voltage Ch 1 [0.01V] (Switch only)		31063	unsinged 32-bit	Voltage Ch 1 [0.01V] (Switch only)		32063	Single Precision Floating Point	Voltage Ch 1 [V] (Switch only)		- For transmit interval bit value 0 -> long tx interval (~20s), bit value 1 -> short tx interval (~2s). NOTE!! Remote Switch device will go to long Tx interval only if all switches are off
30033	unsinged 16-bit	Current Ch 1 [mA] (Switch only)		31065	unsinged 32-bit	Current Ch 1 [mA] (Switch only)		32065	Single Precision Floating Point	Current Ch 1 [mA] (Switch only)
30034	unsinged 16-bit	Voltage Ch 2 [0.01V] (Switch only)		31067	unsinged 32-bit	Voltage Ch 2 [0.01V] (Switch only)		32067	Single Precision Floating Point	Voltage Ch 2 [V] (Switch only)
30035	unsinged 16-bit	Current Ch 2 [mA] (Switch only)		31069	unsinged 32-bit	Current Ch 2 [mA] (Switch only)		32069	Single Precision Floating Point	Current Ch 2 [mA] (Switch only)
30036	unsinged 16-bit	2nd Device Type		31071	unsinged 32-bit	2nd Device Type		32071	Single Precision Floating Point	2nd Device Type		- Remote Switch/MUX implementation has a list that can handle 32 Switches or Muxes
30037	unsinged 16-bit	2nd Device ID		31073	unsinged 32-bit	2nd Device ID		32073	Single Precision Floating Point	2nd Device ID		- New device is added to the first available position for example mux or switch is added to 1st position if list is empty
30038	unsinged 16-bit	Time since last Rx [s]		31075	unsinged 32-bit	Time since last Rx [s]		32075	Single Precision Floating Point	Time since last Rx [s]		or the 1st position of list is available otherwise, i.e. device previously occupied the 1st position has not send packet in 2 minutes
30039	unsinged 16-bit	Switch State		31077	unsinged 32-bit	Switch State		32077	Single Precision Floating Point	Switch State
30040	unsinged 16-bit	Temperature [1/128°C]		31079	unsinged 32-bit	Temperature [1/128°C]		32079	Single Precision Floating Point	Temperature [°C]
30041	unsinged 16-bit	Input Voltage [0.01V]		31081	unsinged 32-bit	Input Voltage [0.01V]		32081	Single Precision Floating Point	Input Voltage [V]
30042	unsinged 16-bit	Voltage Ch 1 [0.01V] (Switch only)		31083	unsinged 32-bit	Voltage Ch 1 [0.01V] (Switch only)		32083	Single Precision Floating Point	Voltage Ch 1 [V] (Switch only)
30043	unsinged 16-bit	Current Ch 1 [mA] (Switch only)		31085	unsinged 32-bit	Current Ch 1 [mA] (Switch only)		32085	Single Precision Floating Point	Current Ch 1 [mA] (Switch only)
30044	unsinged 16-bit	Voltage Ch 2 [0.01V] (Switch only)		31087	unsinged 32-bit	Voltage Ch 2 [0.01V] (Switch only)		32087	Single Precision Floating Point	Voltage Ch 2 [V] (Switch only)
30045	unsinged 16-bit	Current Ch 2 [mA] (Switch only)		31089	unsinged 32-bit	Current Ch 2 [mA] (Switch only)		32089	Single Precision Floating Point	Current Ch 2 [mA] (Switch only)
30046	unsinged 16-bit	3rd Device Type		31091	unsinged 32-bit	3rd Device Type		32091	Single Precision Floating Point	3rd Device Type
30047	unsinged 16-bit	3rd Device ID		31093	unsinged 32-bit	3rd Device ID		32093	Single Precision Floating Point	3rd Device ID
30048	unsinged 16-bit	Time since last Rx [s]		31095	unsinged 32-bit	Time since last Rx [s]		32095	Single Precision Floating Point	Time since last Rx [s]
30049	unsinged 16-bit	Switch State		31097	unsinged 32-bit	Switch State		32097	Single Precision Floating Point	Switch State
30050	unsinged 16-bit	Temperature [1/128°C]		31099	unsinged 32-bit	Temperature [1/128°C]		32099	Single Precision Floating Point	Temperature [°C]
30051	unsinged 16-bit	Input Voltage [0.01V]		31101	unsinged 32-bit	Input Voltage [0.01V]		32101	Single Precision Floating Point	Input Voltage [V]
30052	unsinged 16-bit	Voltage Ch 1 [0.01V] (Switch only)		31103	unsinged 32-bit	Voltage Ch 1 [0.01V] (Switch only)		32103	Single Precision Floating Point	Voltage Ch 1 [V] (Switch only)
30053	unsinged 16-bit	Current Ch 1 [mA] (Switch only)		31105	unsinged 32-bit	Current Ch 1 [mA] (Switch only)		32105	Single Precision Floating Point	Current Ch 1 [mA] (Switch only)
30054	unsinged 16-bit	Voltage Ch 2 [0.01V] (Switch only)		31107	unsinged 32-bit	Voltage Ch 2 [0.01V] (Switch only)		32107	Single Precision Floating Point	Voltage Ch 2 [V] (Switch only)
30055	unsinged 16-bit	Current Ch 2 [mA] (Switch only)		31109	unsinged 32-bit	Current Ch 2 [mA] (Switch only)		32109	Single Precision Floating Point	Current Ch 2 [mA] (Switch only)
...	...	...		...	...	...		...	...	...
30336	unsinged 16-bit	32th Device Type		31671	unsinged 32-bit	32th Device Type		32671	Single Precision Floating Point	32th Device Type
30337	unsinged 16-bit	32th Device ID		31673	unsinged 32-bit	32th Device ID		32673	Single Precision Floating Point	32th Device ID
30338	unsinged 16-bit	Time since last Rx [s]		31675	unsinged 32-bit	Time since last Rx [s]		32675	Single Precision Floating Point	Time since last Rx [s]
30339	unsinged 16-bit	Switch State		31677	unsinged 32-bit	Switch State		32677	Single Precision Floating Point	Switch State
30340	unsinged 16-bit	Temperature [1/128°C]		31679	unsinged 32-bit	Temperature [1/128°C]		32679	Single Precision Floating Point	Temperature [°C]
30341	unsinged 16-bit	Input Voltage [0.01V]		31681	unsinged 32-bit	Input Voltage [0.01V]		32681	Single Precision Floating Point	Input Voltage [V]
30342	unsinged 16-bit	Voltage Ch 1 [0.01V] (Switch only)		31683	unsinged 32-bit	Voltage Ch 1 [0.01V] (Switch only)		32683	Single Precision Floating Point	Voltage Ch 1 [V] (Switch only)
30343	unsinged 16-bit	Current Ch 1 [mA] (Switch only)		31685	unsinged 32-bit	Current Ch 1 [mA] (Switch only)		32685	Single Precision Floating Point	Current Ch 1 [mA] (Switch only)
30344	unsinged 16-bit	Voltage Ch 2 [0.01V] (Switch only)		31687	unsinged 32-bit	Voltage Ch 2 [0.01V] (Switch only)		32687	Single Precision Floating Point	Voltage Ch 2 [V] (Switch only)
30345	unsinged 16-bit	Current Ch 2 [mA] (Switch only)		31689	unsinged 32-bit	Current Ch 2 [mA] (Switch only)		32689	Single Precision Floating Point	Current Ch 2 [mA] (Switch only)

Input Registers (16-bit integer)				Input Registers (32-bit integer)				Input Registers single presicion floating point
2 Channel Qaudrature Measurement values				2 Channel Qaudrature Measurement values				2 Channel Qaudrature Measurement values
Register	Type	Description		Register	Type	Description		Register	Type	Description
30026	unsinged 16-bit	Packe Index		31051	unsinged 32-bit	Packe Index (16-bit value)		32051	Single Precision Floating Point	Packe Index (16-bit value)	<-	Radio incoming Packet Index, or actually running index of the expected incoming packet
30027	unsinged 16-bit	Radio Rx Status		31053	unsinged 32-bit	Radio Rx Status		32053	Single Precision Floating Point	Radio Rx Status	<-	Radio Rx Status: Binary coded Receive Status: Radio 1 has received packet bit 0 -> 1 otherwise 0, Radio 2 has received packet bit 1 -> 1 otherwise 0
30028	unsinged 16-bit	Receive Success [%]		31055	unsinged 32-bit	Receive Success [%]		32055	Single Precision Floating Point	Receive Success [%]
30029	unsinged 16-bit	Measured Samplerate [Hz]		31057	unsinged 32-bit	Measured Samplerate [Hz]		32057	Single Precision Floating Point	Measured Samplerate [Hz]	<-	Quadrature Sample Rate measured from incoming packet frequency
30030	1nsinged 16-bit	Packet Drift Index		31059	unsinged 32-bit	Packet Drift Index		32059	Single Precision Floating Point	Packet Drift Index	<-	Indicator of receiver not been able to adjust timer/couter to incoming packets , i.e. Incoming packets drift (and might be lost). If value is not changed packets are received as expected.
30031	unsinged 16-bit	Reserved		31061	unsinged 32-bit	Reserved		32061	Single Precision Floating Point	Reserved
30032	unsinged 16-bit	Reserved		31063	unsinged 32-bit	Reserved		32063	Single Precision Floating Point	Reserved
30033	unsinged 16-bit	Reserved		31065	unsinged 32-bit	Reserved		32065	Single Precision Floating Point	Reserved
30034	unsinged 16-bit	Reserved		31067	unsinged 32-bit	Reserved		32067	Single Precision Floating Point	Reserved
30035	unsinged 16-bit	Reserved		31069	unsinged 32-bit	Reserved		32069	Single Precision Floating Point	Reserved
30036	singed 16-bit	Channel 1 Value nth value		31071	singed 32-bit	Channel 1 Value nth value		32071	Single Precision Floating Point	Channel 1 Value nth value	<-	Channel 1 nth sample of most recent radio packet, i.e. the most recent sample					NOTE!! 16-bit values will overflow if counter is greater that 32767 or less than -32768 in signed integer and greater than 65535 or less than 0 in unsigned integer
30037	singed 16-bit	Channel 2 Value nth value		31073	singed 32-bit	Channel 2 Value nth value		32073	Single Precision Floating Point	Channel 2 Value nth value	<-	Channel 2 nth sample of most recent radio packet, i.e. the most recent sample					NOTE!! 16-bit values will overflow if counter is greater that 32767 or less than -32768 in signed integer and greater than 65535 or less than 0 in unsigned integer
30038	singed 16-bit	Channel 1 Value (n-1)th value		31075	singed 32-bit	Channel 1 Value (n-1)th value		32075	Single Precision Floating Point	Channel 1 Value (n-1)th value	<-	Channel 1 (n-1)th sample of most recent radio packet					NOTE!! 16-bit values will overflow if counter is greater that 32767 or less than -32768 in signed integer and greater than 65535 or less than 0 in unsigned integer
30039	singed 16-bit	Channel 2 Value (n-1)th value		31077	singed 32-bit	Channel 2 Value (n-1)th value		32077	Single Precision Floating Point	Channel 2 Value (n-1)th value	<-	Channel 2 (n-1)th sample of most recent radio packet					NOTE!! 16-bit values will overflow if counter is greater that 32767 or less than -32768 in signed integer and greater than 65535 or less than 0 in unsigned integer
30040	singed 16-bit	Channel 1 Value (n-2)th value		31079	singed 32-bit	Channel 1 Value (n-2)th value		32079	Single Precision Floating Point	Channel 1 Value (n-2)th value	<-	Channel 1 (n-2)th sample of most recent radio packet					NOTE!! 16-bit values will overflow if counter is greater that 32767 or less than -32768 in signed integer and greater than 65535 or less than 0 in unsigned integer
30041	singed 16-bit	Channel 2 Value (n-2)th value		31081	singed 32-bit	Channel 2 Value (n-2)th value		32081	Single Precision Floating Point	Channel 2 Value (n-2)th value	<-	Channel 2 (n-2)th sample of most recent radio packet					NOTE!! 16-bit values will overflow if counter is greater that 32767 or less than -32768 in signed integer and greater than 65535 or less than 0 in unsigned integer
30042	singed 16-bit	Channel 2 Value (n-3)th value		31083	singed 32-bit	Channel 2 Value (n-3)th value		32083	Single Precision Floating Point	Channel 2 Value (n-3)th value	<-	Channel 1 (n-3)th sample of most recent radio packet					NOTE!! 16-bit values will overflow if counter is greater that 32767 or less than -32768 in signed integer and greater than 65535 or less than 0 in unsigned integer
30043	singed 16-bit	Channel 2 Value (n-3)th value		31085	singed 32-bit	Channel 2 Value (n-3)th value		32085	Single Precision Floating Point	Channel 2 Value (n-3)th value	<-	Channel 2 (n-3)th sample of most recent radio packet					NOTE!! 16-bit values will overflow if counter is greater that 32767 or less than -32768 in signed integer and greater than 65535 or less than 0 in unsigned integer
30044	singed 16-bit	Channel 1 Value (n-4)th value		31087	singed 32-bit	Channel 1 Value (n-4)th value		32087	Single Precision Floating Point	Channel 1 Value (n-4)th value	<-	Channel 1 (n-4)th sample of most recent radio packet					NOTE!! 16-bit values will overflow if counter is greater that 32767 or less than -32768 in signed integer and greater than 65535 or less than 0 in unsigned integer
30045	singed 16-bit	Channel 2 Value (n-4)th value		31089	singed 32-bit	Channel 2 Value (n-4)th value		32089	Single Precision Floating Point	Channel 2 Value (n-4)th value	<-	Channel 2 (n-4)th sample of most recent radio packet					NOTE!! 16-bit values will overflow if counter is greater that 32767 or less than -32768 in signed integer and greater than 65535 or less than 0 in unsigned integer
...	...	...		...	...	...		...	...	...

Holding Registers
Holding Registers (16-bit integer)				Input Registers (32-bit integer)				Input Registers single presicion floating point
RF Device independent Measurement values				RF Device independent Measurement values				RF Device independent Measurement values
Register	Type	Description		Register	Type	Description		Register	Type	Description
40001	unsigned singed 16-bit	Radio Channel (R/W)		41001	unsigned singed 32-bit	Radio Channel (R/W)		42001	Single Precision Floating Point	Radio Channel (R/W)	<-	Radio Channel register: 0..127. Read and Write register
40002	unsigned singed 16-bit	On Air Data Rate (Read Only)		41003	unsigned singed 32-bit	On Air Data Rate (Read Only)		42003	Single Precision Floating Point	On Air Data Rate (Read Only)	<-	On Air Data Rate register: 0 -> 250kbps, 1-> 1Mbps, 2 -> 2Mbps. This is a read only value, any write operations are ignored i.e. no harm is done by writing this register
40003	unsigned singed 16-bit	Radio Device Type (R/W)		41005	unsigned singed 32-bit	Radio Device Type (R/W)		42005	Single Precision Floating Point	Radio Device Type (R/W)	<-	Radio Device Type register: 2 -> 16 Channel Thermocouple, 3 -> 8 Channel Thermocoule, 4 -> Remote Switch/Mux, 5 -> 2 Ch Quadrature, 6 -> 4 Channel Thermocouple. Read and Write register
40004	unsigned singed 16-bit	Device Specific Register 0 (R/W)		41007	unsigned singed 32-bit	Device Specific Register 0 (R/W)		42007	Single Precision Floating Point	Device Specific Register 0 (R/W)	<-	Device Specific Register. Read and Write register
40005	unsigned singed 16-bit	Device Specific Register 1 (R/W)		41009	unsigned singed 32-bit	Device Specific Register 1 (R/W)		42009	Single Precision Floating Point	Device Specific Register 1 (R/W)	<-	Device Specific Register. Read and Write register
40006	unsigned singed 16-bit	Device Specific Register 2 (R/W)		41011	unsigned singed 32-bit	Device Specific Register 2 (R/W)		42011	Single Precision Floating Point	Device Specific Register 2 (R/W)	<-	Device Specific Register. Read and Write register
40007	unsigned singed 16-bit	Device Specific Register 3 (R/W)		41013	unsigned singed 32-bit	Device Specific Register 3 (R/W)		42013	Single Precision Floating Point	Device Specific Register 3 (R/W)	<-	Device Specific Register. Read and Write register
40008	unsigned singed 16-bit	Device Specific Register 4 (R/W)		41015	unsigned singed 32-bit	Device Specific Register 4 (R/W)		42015	Single Precision Floating Point	Device Specific Register 4 (R/W)	<-	Device Specific Register. Read and Write register
40009	unsigned singed 16-bit	Reserved		41017	unsigned singed 32-bit	Reserved		42017	Single Precision Floating Point	Reserved
40010	unsigned singed 16-bit	Reserved		41019	unsigned singed 32-bit	Reserved		42019	Single Precision Floating Point	Reserved
40011	unsigned singed 16-bit	Reserved		41021	unsigned singed 32-bit	Reserved		42021	Single Precision Floating Point	Reserved
40012	unsigned singed 16-bit	Reserved		41023	unsigned singed 32-bit	Reserved		42023	Single Precision Floating Point	Reserved
40013	unsigned singed 16-bit	Reserved		41025	unsigned singed 32-bit	Reserved		42025	Single Precision Floating Point	Reserved
40014	unsigned singed 16-bit	Reserved		41027	unsigned singed 32-bit	Reserved		42027	Single Precision Floating Point	Reserved
40015	unsigned singed 16-bit	Reserved		41029	unsigned singed 32-bit	Reserved		42029	Single Precision Floating Point	Reserved
40016	unsigned singed 16-bit	Reserved		41031	unsigned singed 32-bit	Reserved		42031	Single Precision Floating Point	Reserved
40017	unsigned singed 16-bit	Reserved		41033	unsigned singed 32-bit	Reserved		42033	Single Precision Floating Point	Reserved
40018	unsigned singed 16-bit	Reserved		41035	unsigned singed 32-bit	Reserved		42035	Single Precision Floating Point	Reserved
40019	unsigned singed 16-bit	Reserved		41037	unsigned singed 32-bit	Reserved		42037	Single Precision Floating Point	Reserved
40020	unsigned singed 16-bit	Reserved		41039	unsigned singed 32-bit	Reserved		42039	Single Precision Floating Point	Reserved
40021	unsigned singed 16-bit	Reserved		41041	unsigned singed 32-bit	Reserved		42041	Single Precision Floating Point	Reserved
40022	unsigned singed 16-bit	Reserved		41043	unsigned singed 32-bit	Reserved		42043	Single Precision Floating Point	Reserved
40023	unsigned singed 16-bit	Reserved		41045	unsigned singed 32-bit	Reserved		42045	Single Precision Floating Point	Reserved
40024	unsigned singed 16-bit	Reserved		41047	unsigned singed 32-bit	Reserved		42047	Single Precision Floating Point	Reserved
40025	unsigned singed 16-bit	Reserved		41049	unsigned singed 32-bit	Reserved		42049	Single Precision Floating Point	Reserved

Holding Registers (16-bit integer)				Holding Registers (32-bit integer)				Holding Registers single presicion floating point
Thermo Couple 8 and 16 Channel Measurement values				Thermo Couple 8 and 16 Channel Measurement values				Thermo Couple 8 and 16 Channel Measurement values
Register	Type	Description		Register	Type	Description		Register	Type	Description
40004	unsigned singed 16-bit	Device Specific Register 0 (R/W)		41007	unsigned singed 32-bit	Device Specific Register 0 (R/W)		42007	Single Precision Floating Point	Device Specific Register 0 (R/W)	<-	If value of Device Specific Register 0 is 49
40005	unsigned singed 16-bit	Device Specific Register 1 (R/W)		41009	unsigned singed 32-bit	Device Specific Register 1 (R/W)		42009	Single Precision Floating Point	Device Specific Register 1 (R/W)	<-	then Device Specific Register 1 value indicates of number consecutive samples that must be received to validate data
40006	unsigned singed 16-bit	Device Specific Register 2 (R/W)		41011	unsigned singed 32-bit	Device Specific Register 2 (R/W)		42011	Single Precision Floating Point	Device Specific Register 2 (R/W)	<-	then Device Specific Register 2 indicates of number consecutive samples that must be missed to invalidate data

Holding Registers (16-bit integer)				Holding Registers (32-bit integer)				Holding Registers single presicion floating point
Thermo Couple 4 Channel Measurement values				Thermo Couple 4 Channel Measurement values				Thermo Couple 4 Channel Measurement values
Register	Type	Description		Register	Type	Description		Register	Type	Description
40004	unsigned singed 16-bit	Device Specific Register 0 (R/W)		41007	unsigned singed 32-bit	Device Specific Register 0 (R/W)		42007	Single Precision Floating Point	Device Specific Register 0 (R/W)	<-	If value of Device Specific Register 0 is 49
40005	unsigned singed 16-bit	Device Specific Register 1 (R/W)		41009	unsigned singed 32-bit	Device Specific Register 1 (R/W)		42009	Single Precision Floating Point	Device Specific Register 1 (R/W)	<-	then Device Specific Register 1 value indicates of number consecutive samples that must be received to validate data
40006	unsigned singed 16-bit	Device Specific Register 2 (R/W)		41011	unsigned singed 32-bit	Device Specific Register 2 (R/W)		42011	Single Precision Floating Point	Device Specific Register 2 (R/W)	<-	then Device Specific Register 2 indicates of number consecutive samples that must be missed to invalidate data

Holding Registers (16-bit integer)				Holding Registers (32-bit integer)				Holding Registers single presicion floating point
Remote Mux/Switch				Remote Mux/Switch				Remote Mux/Switch
Register	Type	Description		Register	Type	Description		Register	Type	Description
40004	unsigned singed 16-bit	Device Specific Register 0 (R/W)		41007	unsigned singed 32-bit	Device Specific Register 0 (R/W)		42007	Single Precision Floating Point	Device Specific Register 0 (R/W)	<-	If bit 0 in Device Specific Register 0 is 1 then Global Switch State register controls every device's Switch State register bits 0...6.
...	...	...		...	...	...		...	...	...		If bit 1 in Device Specific Register 0 register is 1 then Global Switch State register controls every devices bit 7 in Switch State register
40025	unsigned singed 16-bit	Global Switch State		41049	unsigned singed 32-bit	Global Switch State		42049	Single Precision Floating Point	Global Switch State	<-	Global Switch State register, look above. Read and Write register. Buttons 1 and 2 control bits in this register if bits 0 and/or 1 are set in Device Specific Register 0: Button 1 toggles bits 0..6 and Button 2 toggles bit 7
40026	unsinged 16-bit	1st Device Type (R0)		41051	unsinged 32-bit	1st Device Type (R0)		42051	Single Precision Floating Point	1st Device Type (R0)	<-	Device Type register: 1 -> Switch, 2 -> Mux. Read only register, write operation will be ignored
40027	unsinged 16-bit	1st Device ID (RO)		41053	unsinged 32-bit	1st Device ID (RO)		42053	Single Precision Floating Point	1st Device ID (RO)	<-	Device Id register. Read only register, write operation will be ignored
40028	unsinged 16-bit	Switch State (R/W)		41055	unsinged 32-bit	Switch State (R/W)		42055	Single Precision Floating Point	Switch State (R/W)	<-	Device specific Switch State register. Read and Write register. Bits 0..6 control the physical switch or mux states and bit 7 controls the transmit interval.
40029	unsinged 16-bit	reserved		41057	unsinged 32-bit	reserved		42057	Single Precision Floating Point	reserved		- For switches bit value 0 -> switch off, bit value 1 -> switch on.
40030	unsinged 16-bit	reserved		41059	unsinged 32-bit	reserved		42059	Single Precision Floating Point	reserved		- For muxes bit value 0 -> CH1 selected , bit value 1 -> CH2 selected
40031	unsinged 16-bit	reserved		41061	unsinged 32-bit	reserved		42061	Single Precision Floating Point	reserved		- For transmit interval bit value 0 -> long tx interval (~20s), bit value 1 -> short tx interval (~2s). NOTE!! Remote Switch device will go to long Tx interval only if all switches are off
40032	unsinged 16-bit	reserved		41063	unsinged 32-bit	reserved		42063	Single Precision Floating Point	reserved
40033	unsinged 16-bit	reserved		41065	unsinged 32-bit	reserved		42065	Single Precision Floating Point	reserved
40034	unsinged 16-bit	reserved		41067	unsinged 32-bit	reserved		42067	Single Precision Floating Point	reserved
40035	unsinged 16-bit	reserved		41069	unsinged 32-bit	reserved		42069	Single Precision Floating Point	reserved
40036	unsinged 16-bit	2nd Device Type (R0)		41071	unsinged 32-bit	2nd Device Type (R0)		42071	Single Precision Floating Point	2nd Device Type (R0)
40037	unsinged 16-bit	2ndDevice ID (RO)		41073	unsinged 32-bit	2ndDevice ID (RO)		42073	Single Precision Floating Point	2ndDevice ID (RO)
40038	unsinged 16-bit	Switch State (R/W)		41075	unsinged 32-bit	Switch State (R/W)		42075	Single Precision Floating Point	Switch State (R/W)	<-	Device specific Switch State register. Read and Write register. Bits 0..6 control the physical switch or mux states and bit 7 controls the transmit interval.
40039	unsinged 16-bit	reserved		41077	unsinged 32-bit	reserved		42077	Single Precision Floating Point	reserved		- For switches bit value 0 -> switch off, bit value 1 -> switch on.
40040	unsinged 16-bit	reserved		41079	unsinged 32-bit	reserved		42079	Single Precision Floating Point	reserved		- For muxes bit value 0 -> CH1 selected , bit value 1 -> CH2 selected
40041	unsinged 16-bit	reserved		41081	unsinged 32-bit	reserved		42081	Single Precision Floating Point	reserved		- For transmit interval bit value 0 -> long tx interval (~20s), bit value 1 -> short tx interval (~2s). NOTE!! Remote Switch device will go to long Tx interval only if all switches are off
40042	unsinged 16-bit	reserved		41083	unsinged 32-bit	reserved		42083	Single Precision Floating Point	reserved
40043	unsinged 16-bit	reserved		41085	unsinged 32-bit	reserved		42085	Single Precision Floating Point	reserved
40044	unsinged 16-bit	reserved		41087	unsinged 32-bit	reserved		42087	Single Precision Floating Point	reserved
40045	unsinged 16-bit	reserved		41089	unsinged 32-bit	reserved		42089	Single Precision Floating Point	reserved
40046	unsinged 16-bit	3rd Device Type (R0)		41091	unsinged 32-bit	3rd Device Type (R0)		42091	Single Precision Floating Point	3rd Device Type (R0)
40047	unsinged 16-bit	3rd Device ID (RO)		41093	unsinged 32-bit	3rd Device ID (RO)		42093	Single Precision Floating Point	3rd Device ID (RO)
40048	unsinged 16-bit	Switch State (R/W)		41095	unsinged 32-bit	Switch State (R/W)		42095	Single Precision Floating Point	Switch State (R/W)	<-	Device specific Switch State register. Read and Write register. Bits 0..6 control the physical switch or mux states and bit 7 controls the transmit interval.
40049	unsinged 16-bit	reserved		41097	unsinged 32-bit	reserved		42097	Single Precision Floating Point	reserved		- For switches bit value 0 -> switch off, bit value 1 -> switch on.
40050	unsinged 16-bit	reserved		41099	unsinged 32-bit	reserved		42099	Single Precision Floating Point	reserved		- For muxes bit value 0 -> CH1 selected , bit value 1 -> CH2 selected
40051	unsinged 16-bit	reserved		41101	unsinged 32-bit	reserved		42101	Single Precision Floating Point	reserved		- For transmit interval bit value 0 -> long tx interval (~20s), bit value 1 -> short tx interval (~2s). NOTE!! Remote Switch device will go to long Tx interval only if all switches are off
40052	unsinged 16-bit	reserved		41103	unsinged 32-bit	reserved		42103	Single Precision Floating Point	reserved
...	...	...		...	...	...		...	...	...
40336	unsinged 16-bit	32nd Device Type (R0)		41671	unsinged 32-bit	32nd Device Type (R0)		42671	Single Precision Floating Point	32nd Device Type (R0)
40337	unsinged 16-bit	32nd Device ID (RO)		41673	unsinged 32-bit	32nd Device ID (RO)		42673	Single Precision Floating Point	32nd Device ID (RO)
40338	unsinged 16-bit	Switch State (R/W)		41675	unsinged 32-bit	Switch State (R/W)		42675	Single Precision Floating Point	Switch State (R/W)	<-	Device specific Switch State register. Read and Write register. Bits 0..6 control the physical switch or mux states and bit 7 controls the transmit interval.
40339	unsinged 16-bit	reserved		41677	unsinged 32-bit	reserved		42677	Single Precision Floating Point	reserved		- For switches bit value 0 -> switch off, bit value 1 -> switch on.
40340	unsinged 16-bit	reserved		41679	unsinged 32-bit	reserved		42679	Single Precision Floating Point	reserved		- For muxes bit value 0 -> CH1 selected , bit value 1 -> CH2 selected
40341	unsinged 16-bit	reserved		41681	unsinged 32-bit	reserved		42681	Single Precision Floating Point	reserved		- For transmit interval bit value 0 -> long tx interval (~20s), bit value 1 -> short tx interval (~2s). NOTE!! Remote Switch device will go to long Tx interval only if all switches are off
40342	unsinged 16-bit	reserved		41683	unsinged 32-bit	reserved		42683	Single Precision Floating Point	reserved
40343	unsinged 16-bit	reserved		41685	unsinged 32-bit	reserved		42685	Single Precision Floating Point	reserved
40344	unsinged 16-bit	reserved		41687	unsinged 32-bit	reserved		42687	Single Precision Floating Point	reserved
40345	unsinged 16-bit	reserved		41689	unsinged 32-bit	reserved		42689	Single Precision Floating Point	reserved

Holding Registers (16-bit integer)				Holding Registers (32-bit integer)				Holding Registers single presicion floating point
2 Channel Qaudrature Measurement values				2 Channel Qaudrature Measurement values				2 Channel Qaudrature Measurement values
Register	Type	Description		Register	Type	Description		Register	Type	Description
40026	unsinged 16-bit	PWM Frequency [Hz] (R/W)		41051	unsinged 32-bit	PWM Frequency [Hz] (R/W)		42051	Single Precision Floating Point	PWM Frequency [Hz] (R/W)	<-	PWM frequency set value. This is a Read and Write register, but for all purposes use 10kHz
40027	singed 16-bit	RX PLL Control Value High (R/W)		41053	singed 32-bit	RX PLL Control Value High (R/W)		42053	Single Precision Floating Point	RX PLL Control Value High (R/W)	<-	Adjustable PWM Frequency counter max shift value. i.e. PWM_Freq_Min = PWM_Clock / ((PWM_Clock / PWM_Freq_Set) + RX_PLL_Control_Value_High)
40028	singed 16-bit	RX PLL Control Value Low (R/W)		41055	singed 32-bit	RX PLL Control Value Low (R/W)		42055	Single Precision Floating Point	RX PLL Control Value Low (R/W)	<-	Adjustable PWM Frequency counter min shift value. i.e. PWM_Freq_Max = PWM_Clock / ((PWM_Clock / PWM_Freq_Set) + RX_PLL_Control_Value_Low). Note!!! RX PLL Control Value Low should be negative!!!!!
40029	unsinged 16-bit	Channel 1 Counter Max Value (R/W)		41057	unsinged 32-bit	Channel 1 Counter Max Value (R/W)		42057	Single Precision Floating Point	Channel 1 Counter Max Value (R/W)	<-	Quadrature Counter Max register. Read and Write register. PWM duty cycle is calculated with equation PWM_DC = (Counter_value + 50%_OffsetValue - Counter_Min) / (Counter_Max - Counter_Min) * 100%
40030	1nsinged 16-bit	Channel 1 Counter Min Value (R/W)		41059	unsinged 32-bit	Channel 1 Counter Min Value (R/W)		42059	Single Precision Floating Point	Channel 1 Counter Min Value (R/W)	<-	Quadrature Counter Min register. Read and Write register. PWM duty cycle is calculated with equation PWM_DC = (Counter_value + 50%_OffsetValue - Counter_Min) / (Counter_Max - Counter_Min) * 100%
40031	unsinged 16-bit	Channel 1 50% Duty Cycle Value1 (R/W)		41061	unsinged 32-bit	Channel 1 50% Duty Cycle Value1 (R/W)		42061	Single Precision Floating Point	Channel 1 50% Duty Cycle Value1 (R/W)	<-	50% duty cycle Quadrature counter value register. Read and Write regsiter. Value used to set 50% pwm duty cycle to certain quadrature counter value.
40032	unsinged 16-bit	Channel 1 Counter Mode2 (R/W)		41063	unsinged 32-bit	Channel 1 Counter Mode2 (R/W)		42063	Single Precision Floating Point	Channel 1 Counter Mode2 (R/W)	<-	PWM Counter Mode register. Read and Write regsiter.
40033	unsinged 16-bit	Channel 2 Counter Max Value (R/W)		41065	unsinged 32-bit	Channel 2 Counter Max Value (R/W)		42065	Single Precision Floating Point	Channel 2 Counter Max Value (R/W)	<-	Quadrature Counter Max register. Read and Write register. PWM duty cycle is calculated with equation PWM_DC = (Counter_value + 50%_OffsetValue - Counter_Min) / (Counter_Max - Counter_Min) * 100%
40034	unsinged 16-bit	Channel 2 Counter Min Value (R/W)		41067	unsinged 32-bit	Channel 2 Counter Min Value (R/W)		42067	Single Precision Floating Point	Channel 2 Counter Min Value (R/W)	<-	Quadrature Counter Min register. Read and Write register. PWM duty cycle is calculated with equation PWM_DC = (Counter_value + 50%_OffsetValue - Counter_Min) / (Counter_Max - Counter_Min) * 100%
40035	unsinged 16-bit	Channel 2 50% Duty Cycle Value1 (R/W)		41069	unsinged 32-bit	Channel 2 50% Duty Cycle Value1 (R/W)		42069	Single Precision Floating Point	Channel 2 50% Duty Cycle Value1 (R/W)	<-	50% duty cycle Quadrature counter value register. Read and Write regsiter. Value used to set 50% pwm duty cycle to certain quadrature counter value.
40036	unsinged 16-bit	Channel 2 Counter Mode2 (R/W)		41071	unsinged 32-bit	Channel 2 Counter Mode2 (R/W)		42071	Single Precision Floating Point	Channel 2 Counter Mode2 (R/W)	<-	PWM Counter Mode register. Read and Write regsiter.
1 50% Duty Cycle Value offsets the counter value that produces the 50% offset: Counter Max Value and Counter Min Value defines the range and 50% Duty Cycle Value offset. i.e. value in 24-bit space what produced 50% PWM Duty Cycle (Quadrature counter is 24-bit long)
2 Counter Mode register: If bit 0 is set counter is in Saturated Mode, i.e. values outside values space defined by Counter Max Value, Counter Min Value and 50% Duty Cycle Value are satureted to 0% and 100% duty cycle
If bit 1 is set 50% Duty Cycle Value is used (Modbus Forces the bit 1 to be set) Bit 7 controls the Fixed vs Adjustable PWM frequency (Frequency either follows the incoming packet frequency of not)
If bit 7 is set PWM frequency is fixed otherwise PWM frequency is adjusted to follow incoming radio packets. If fixed PWM Freq not used